{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["冷冻水系统","热水供水","Sheet1"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"冷冻水系统","index":0,"n_rows":28,"n_cols":53,"rows_kept":28,"merged":[[0,1,0,2],[0,7,0,19],[0,20,0,28],[0,29,0,34],[0,35,0,39],[0,40,0,46],[0,47,0,50],[1,1,1,2],[1,7,1,19],[1,20,1,28],[1,29,1,34],[1,35,1,39],[2,1,2,2],[4,4,17,4],[4,5,17,5],[19,4,26,4],[19,5,26,5]],"flags":["formulas_cached_only"]}
[null,"设备名称",null,"设备编号","位置","PLC箱编号","数量","模拟量输入",{"$nulls":12},"数字量输入",{"$nulls":8},"模拟量输出",{"$nulls":5},"数字量输出",{"$nulls":4},"集成",{"$nulls":6},"小计",{"$nulls":3},"总计"]
[null,"Equipment",null,"Number","Location","DDC Number","Qty","AI",{"$nulls":12},"DI",{"$nulls":8},"AO",{"$nulls":5},"DO",{"$nulls":11},"AI","DI","AO","DO","TOTAL"]
[{"$nulls":7},"室外温湿度","室内温湿度","送风温度","回风温度","水流量","供水温度","回水温度","冷却塔出水温度","频率反馈","供水压力","回水压力","液位计","CO2浓度","运行状态","故障报警","手动或自动状态/本地或远程控制","碟阀开关反馈","高低水位","水流开关状态","高温报警","滤网报警","缺风报警","两通冷水阀","变频调节","三通阀调节","旁通阀调节","回风风阀","新风风阀","设备启停","蝶阀开关控制","电动风阀","复位信号","状态输出","电导仪","风柜通讯","热水供水通讯","冷热量表","水泵通讯","主机通讯","电表"]
[null,"一、冷源站系统"]
[null,1,"冷水主机",null,"冷站房","PLC1",3,{"$nulls":13},3,3,4,8,{"$nulls":11},3,8,{"$nulls":8},3,3,0,18,0,11,29,"主机3，电动阀4"]
[null,2,"冷冻水泵",{"$nulls":3},5,{"$nulls":13},5,5,5,{"$nulls":12},5,{"$nulls":10},5,0,15,0,5,20]
[null,3,"冷冻水泵（变频）",{"$nulls":3},1,{"$nulls":8},1,{"$nulls":4},1,1,1,{"$nulls":7},1,{"$nulls":4},1,{"$nulls":10},1,1,3,1,1,6]
[null,4,"冷却水泵",{"$nulls":3},5,{"$nulls":13},5,5,5,{"$nulls":12},5,{"$nulls":10},5,0,15,0,5,20]
[null,5,"冷却水泵（变频）",{"$nulls":3},1,{"$nulls":8},1,{"$nulls":4},1,1,1,{"$nulls":7},1,{"$nulls":4},1,{"$nulls":10},1,1,3,1,1,6]
[null,6,"冷却塔（变频）",{"$nulls":3},3,{"$nulls":6},3,null,3,{"$nulls":4},3,3,9,12,{"$nulls":6},3,{"$nulls":4},3,12,{"$nulls":9},3,6,27,3,15,51,"塔出水温度3，电动阀6"]
[null,7,"冷冻供水主管",{"$nulls":3},1,{"$nulls":15},4,8,{"$nulls":12},8,{"$nulls":6},1,{"$nulls":3},0,12,0,8,20,"电动阀2"]
[null,8,"冷却供水主管",{"$nulls":3},1,{"$nulls":15},4,8,{"$nulls":12},8,{"$nulls":6},1,{"$nulls":3},0,12,0,8,20,"电动阀2"]
[null,9,"集水器",{"$nulls":3},1,{"$nulls":5},2,2,null,null,2,2,{"$nulls":29},8,0,0,0,8]
[null,10,"分水器",{"$nulls":3},1,{"$nulls":5},2,2,null,null,2,2,{"$nulls":29},8,0,0,0,8]
[null,11,"在线清洗机",{"$nulls":3},1,{"$nulls":33},1,{"$nulls":6},0,0,0,0,0]
[null,12,"室外环境",{"$nulls":3},1,2,{"$nulls":39},2,0,0,0,2]
[null,13,"风柜通讯",{"$nulls":3},5,{"$nulls":34},5,{"$nulls":5},0,0,0,0,0]
[null,14,"小计",{"$nulls":3},29,2,0,0,0,0,4,7,0,5,4,4,0,0,18,18,33,36,0,0,0,0,0,0,5,0,0,0,0,18,36,0,0,0,1,5,null,2,0,3,18,26,105,5,54,190]
[null,"二、采暖站系统"]
[null,1,"真空锅炉",null,"采暖站房","PLC2",3,{"$nulls":38},2,2,0,0,0,0,0]
[null,2,"采暖泵（变频）",{"$nulls":3},3,{"$nulls":37},3,null,3,0,0,0,0,0]
[null,3,"空气源热泵",{"$nulls":3},6,{"$nulls":38},6,2,0,0,0,0,0]
[null,4,"热水供水通讯",{"$nulls":3},3,{"$nulls":35},3,{"$nulls":4},0,0,0,0,0,"两个区域各一个电表（4+2台热泵）"]
[null,5,"集水器",{"$nulls":3},1,{"$nulls":5},2,2,null,null,2,2,{"$nulls":4},8,8,{"$nulls":12},8,{"$nulls":10},8,16,0,8,32]
[null,6,"分水器",{"$nulls":3},1,{"$nulls":5},2,2,null,null,2,2,{"$nulls":4},8,8,{"$nulls":12},8,{"$nulls":10},8,16,0,8,32]
[null,7,"冷水液位",{"$nulls":3},1,{"$nulls":11},1,{"$nulls":28},1,0,0,0,1]
[null,8,"小计",{"$nulls":3},18,0,0,0,0,0,4,4,0,0,4,4,1,0,0,0,16,16,0,0,0,0,0,0,0,0,0,0,0,0,16,0,0,0,0,0,3,0,3,8,7,17,32,0,16,65]
[null,"总计",{"$nulls":4},47,2,0,0,0,0,8,11,0,5,8,8,1,0,18,18,49,52,0,0,0,0,0,0,5,0,0,0,0,18,52,0,0,0,1,5,3,2,3,11,25,43,137,5,70,255]

{"sheet":"热水供水","index":1,"n_rows":11,"n_cols":33,"rows_kept":11,"merged":[[0,1,0,32],[1,1,1,32],[2,1,2,2],[2,7,2,12],[2,13,2,17],[2,18,2,22],[2,23,2,27],[2,28,2,31],[3,1,3,2],[3,7,3,12],[3,13,3,17],[3,18,3,22],[3,23,3,27],[4,1,4,2],[5,4,7,4],[10,1,10,32]],"flags":["formulas_cached_only"]}
[]
[null,"热水供水系统"]
[null,"设备名称",null,"设备编号","位置","DDC箱编号","数量","模拟量输入",{"$nulls":5},"数字量输入",{"$nulls":4},"模拟量输出",{"$nulls":4},"数字量输出",{"$nulls":4},"小计",{"$nulls":3},"总计"]
[null,"Equipment",null,"Number","Location","DDC Number","Qty","AI",{"$nulls":5},"DI",{"$nulls":4},"AO",{"$nulls":4},"DO",{"$nulls":4},"AI","DI","AO","DO","TOTAL"]
[{"$nulls":7},"供水温度","回水温度","频率反馈","供水压力","回水压力","液位","运行状态","故障报警","手动或自动状态","高低水位","水流开关状态","变频调节","三通阀调节","旁通阀调节","回风风阀","新风风阀","设备启停","液位设置","电动风阀","复位信号","状态输出"]
[null,1,"水泵",null,"综合站空压机房",null,8,null,null,8,{"$nulls":3},8,8,{"$nulls":3},8,{"$nulls":4},8,{"$nulls":4},8,16,8,8,40]
[null,2,"温度",{"$nulls":3},8,4,4,{"$nulls":19},8,0,0,0,8]
[null,3,"压力",{"$nulls":3},8,{"$nulls":3},4,4,{"$nulls":16},8,0,0,0,8]
[null,4,"水箱",{"$nulls":3},2,{"$nulls":5},2,{"$nulls":11},2,{"$nulls":3},2,0,0,2,4]
[null,"总计",{"$nulls":4},26,4,4,8,4,4,0,8,8,0,0,0,8,0,0,0,0,8,0,0,0,0,26,16,8,10,60]
[null,"1、分4个区域供水，水泵1用1备。\n2、压力表采用压力传感器，2线制，\n3、温度采用PT100，2线制，\n4、触摸屏显示供回水压力、温度、液位。设置供水压力、频率、液位。水泵有手自动模式，自动为根据压力变频，手动为设定固定频率。\n5、水泵分别为15KW、11KW、4KW、2KW各2台。\n6、提供给上位机，具有同屏幕数据及控制。"]

{"sheet":"Sheet1","index":2,"n_rows":16,"n_cols":51,"rows_kept":16,"merged":[[0,1,0,44],[1,1,1,44],[2,1,2,2],[2,7,2,19],[2,20,2,28],[2,29,2,34],[2,35,2,39],[2,40,2,43],[3,1,3,2],[3,7,3,19],[3,20,3,28],[3,29,3,34],[3,35,3,39],[4,1,4,2],[6,4,14,4]],"flags":["formulas_cached_only"]}
[]
[null,"空压机系统"]
[null,"设备名称",null,"设备编号","位置","DDC箱编号","数量","模拟量输入",{"$nulls":12},"数字量输入",{"$nulls":8},"模拟量输出",{"$nulls":5},"数字量输出",{"$nulls":4},"小计",{"$nulls":3},"总计"]
[null,"Equipment",null,"Number","Location","DDC Number","Qty","AI",{"$nulls":12},"DI",{"$nulls":8},"AO",{"$nulls":5},"DO",{"$nulls":4},"AI","DI","AO","DO","TOTAL"]
[{"$nulls":7},"气体压力","气体温度","气体流量","露点温度","水流量","供水温度","回水温度","冷却塔出水温度","频率反馈","供水压力","回水压力","液位","CO2浓度","运行状态","故障报警","手动或自动状态","碟阀开关反馈","高低水位","水流开关状态","高温报警","滤网报警","缺风报警","两通冷水阀","变频调节","三通阀调节","旁通阀调节","回风风阀","新风风阀","设备启停","蝶阀开关控制","电动风阀","复位信号","状态输出"]
[null,"一、空压站系统"]
[null,1,"空压机",null,"综合站空压机房",null,5,{"$nulls":13},5,5,{"$nulls":13},5,{"$nulls":4},0,10,0,5,15]
[null,2,"冷干机",{"$nulls":3},5,{"$nulls":13},5,5,{"$nulls":18},0,10,0,0,10]
[null,3,"空压机出气总管",{"$nulls":3},1,1,{"$nulls":32},1,0,0,0,1]
[null,4,"冷干机出气总管",{"$nulls":3},1,1,{"$nulls":32},1,0,0,0,1]
[null,5,"储气罐出气总管",{"$nulls":3},1,1,1,1,1,{"$nulls":29},4,0,0,0,4]
[null,6,"二厂压缩空气总管",{"$nulls":3},1,1,null,1,{"$nulls":13},2,{"$nulls":12},1,{"$nulls":3},2,2,0,1,5]
[null,7,"供三线外网总管",{"$nulls":3},1,{"$nulls":16},4,{"$nulls":12},2,{"$nulls":3},0,4,0,2,6]
[null,8,"冷却塔",{"$nulls":3},3,{"$nulls":13},3,3,3,{"$nulls":12},3,{"$nulls":4},0,9,0,3,12]
[null,9,"循环水泵",{"$nulls":3},3,{"$nulls":13},3,3,3,{"$nulls":12},3,{"$nulls":4},0,9,0,3,12,null,null,2611,2721,3721,3731]
[null,"总计",{"$nulls":5},4,1,2,1,0,0,0,0,0,0,0,0,0,16,16,6,6,0,0,0,0,0,0,0,0,0,0,0,11,3,0,0,0,8,44,0,14,66,null,null,1,1,2,2]